## Laingsburg
COMPLIANCE SAMPLE RESULTS FOR WATER (July 2015- June 2016)
Laingsburg |  |  | 2014 Blue Drop Limits | Compliance Calculations |  |  |  |  | 08/07/2015 |  |  |  | 05/08/2015 |  |  |  | 10/09/2015 |  |  |  | 06/10/2015 |  |  |  | 07/11/2015
Parameter | Unit | Risk | Standard Limits (SANS 241-2011 and SANS 241-2006 Class I) | Total Number of Samples | Number of Samples Complying | % Compliance Achieved | Performance | Average | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Goldnerville House | School Tap | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Municipal Tap | Goldnerville House | School Tap | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Goldnerville House | School Tap | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Goldnerville House | School Tap | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Goldnerville Reservoir | School Tap | Goldnerville House | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Goldnerville House | School Tap | Goldnerville Res. | Bergsig Tap | School Res. | Main Res. | Matjiesfontein Tap | Goldnerville House | School Tap | Goldnerville Res. | Bergsig Tap | School Res. | Main Res.
pH (at 25°C) | pH |  | >5.0 - < 9.7 | 20 | 20 | 100% | Excellent | 7.62 | 7.8 | 7.6 | 7.8 | 7.5 | 7.81 | 7.84 | 7.93 | 7.71 | 6.76 | 6.64 | 6.84 | 6.61 | 8.35 | 8.26 | 8.3 | 8.21 | 7.62 | 7.5 | 7.81 | 7.51
Conductivity | mS/m | Aesthetic | < 170 | 20 | 20 | 100% | Exellent | 144.3 | 143 | 138 | 140 | 139 | 156 | 138 | 152 | 138 | 144 | 137 | 136 | 138 | 160 | 151 | 166 | 153 | 139 | 140 | 139 | 139
Langelier Saturation Index |  |  | -
Turbidity | NTU | Operational | < 1 | 20 | 20 | 100% | Exellent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Aesthetic | < 5 | 20 | 20 | 100% | Exellent |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Colour (as Pt) | mg/L Pt-Co | Aesthetic | < 20 | 3 | 3 | 100% | Exellent | 0
CaCO3 Precipitation Potential |  |  | - | 0 |  | #DIV/0!
Total Alkalinity (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Total Hardness (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Calcium Hardness (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Calcium (as Ca) | mg/L | Aesthetic / Operation | < 150 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Magnesium Hardness (as CaCO3) |  |  | - | 0 |  | #DIV/0!
Magnesium (as Mg) | mg/L | Aesthetic / Health | < 70 | 0 | 0 | #DIV/0! | Exellent | #DIV/0!
Fluoride (as F) | mg/L | Chronic Health | < 1.5 | 20 | 0 | 0% | Exellent | 0.604 | 0.92 | 0.91 | 0.83 | 0.92 | 0.46 | 0.66 | 0.54 | 0.65 | 0.59 | 0.63 | 0.66 | 0.59 | 0.51 | 0.56 | 0.49 | 0.52 | 0.4 | 0.41 | 0.41 | 0.42
Total Dissolved Solids | mg/L | Aesthetic | < 1 200 | 0 | 0 | #DIV/0!
Free Chlorine |  | Chronic Health | > 0 - < 0.5 | 20 | 0 | 0% | unacceptable | 0.4065 | 0.36 | 0.34 | 0.37 | 0.13 | 0.34 | 0.36 | 0.45 | 0.5 | 0.35 | 0.53 | 0.38 | 0.53 | 0.02 | 0.32 | 0.17 | 0.32 | 0.64 | 0.63 | 0.73 | 0.66
Iron (as Fe) | ug/L | Chronic Health | < 2 000 | 20 | 20 | 100% | Exellent | 0.0545 | 0.05 | 0.05 | 0.05 | 0.05 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.56 | 0.03 | 0.03 | 0 | 0 | 0 | 0
|  | Aesthetic | < 300 | 20 | 20 | 100% | Exellent |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.56 | 0.03 | 0.03 | 0 | 0 | 0 | 0
Manganese (as Mn) | ug/L | Chronic Health | < 500 | 20 | 20 | 100% | Exellent | 0 | 0.002 | 0.002 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Aesthetic | < 100 | 20 | 20 | 100% | Exellent |  | 0.002 | 0.002 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aluminium (as Al) | ug/L | Operational | < 300 | 16 | 16 | 100% | Exellent | 0.0030625 | 0 | 0 | 0 | 0 |  |  |  |  | 0.013 | 0.01 | 0.012 | 0.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Escherichia Coli | cfu/100ml | Acute Health - 1 | < 0 | 20 | 20 | 100% | Exellent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Coliform Bacteria | cfu/100ml | Operational | < 10 | 20 | 18 | 90% | unacceptable | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 147
Heterotrophic Plate Count | cfu/ml | Operational | < 1000 |  |  | #DIV/0! |  | #DIV/0!
Total Chlorine | mg/L | Chronic Health | < 5 | 0 | 0 | #DIV/0! |  | #DIV/0!
Dissolved Organic Carbon | mg/L | Chronic Health | < 10 | 20 | 8 | 40% | unacceptable | 14.21 | 20.6 | 16.9 | 16.3 | 20.2 | 19.2 | 32.2 | 23.6 | 30.9 | 5.5 | 4.9 | 5.3 | 5.1 | 5.8 | 5.4 | 5.6 | 5.3 | 14.4 | 17.3 | 13.8 | 15.9
Sodium (as Na) | mg/L | Aesthetic | < 200 | 20 | 19 | 95% | Good | 178.389 | 178.37 | 179.71 | 171.62 | 176.1 | 153.43 | 154.5 | 156.6 | 153.34 | 178.46 | 169.94 | 175.87 | 168.82 | 208.53 | 195.99 | 190.32 | 188.25 | 189.64 | 192.78 | 191.06 | 194.45
Potassium (as K) | mg/L | Operational / Health | < 50 | 0 | 0 | #DIV/0! |  | #DIV/0!
Zinc (as Zn) | mg/L | Aesthetic | < 5 | 20 | 20 | 100% | Exellent | 0.0256 | 0.005 | 0.004 | 0.002 | 0.001 | 0.05 | 0.06 | 0.06 | 0.06 | 0.02 | 0.06 | 0.03 | 0.02 | 0 | 0.03 | 0 | 0 | 0.03 | 0.04 | 0.02 | 0.02
Chloride (as Cl) | mg/L | Aesthetic | < 300 | 20 | 20 | 100% | Exellent | 203.9225 | 193 | 168 | 179 | 168 | 263 | 168 | 231 | 176 | 202.45 | 178.1 | 187.18 | 148.66 | 296.59 | 230.76 | 264.76 | 192.06 | 199.64 | 229.78 | 226.59 | 175.88
Sulphate (as SO42-) | mg/L | Acute Health - 1 | < 500 | 20 | 20 | 100% | Exellent | 157.776 | 167.46 | 162.27 | 161.61 | 162.09 | 160.08 | 133.16 | 154.99 | 133.22 | 155.88 | 145.27 | 156.87 | 141.26 | 179.92 | 162.53 | 179.41 | 158.25 | 160.63 | 158.2 | 160.67 | 161.75
|  | Aesthetic | < 250 | 20 | 20 | 100% | Exellent |  | 167.5 | 162.3 | 161.61 | 162.09 | 160.1 | 133.2 | 154.99 | 133.22 | 155.9 | 145.3 | 156.9 | 141.3 | 179.92 | 162.53 | 179.41 | 158.25 | 160.63 | 158.2 | 160.67 | 161.75
Ammonia Nitrogen (as N) | mg/L | Aesthetic | < 1.5 | 20 | 0 | 0% | Exellent | 0.30715 | 0.433 | 0.244 | 0.271 | 0.247 | 0.24 | 0.22 | 0.23 | 0.22 | 0.32 | 0.32 | 0.29 | 0.32 | 0.38 | 0.38 | 0.41 | 0.38 | 0.368 | 0.332 | 0.324 | 0.214
Nitrate as N | mg/L | Acute Health - 1 | < 11 | 20 | 20 | 100% | Exellent | 0.3167 | 0.675 | 0.233 | 0.856 | 0.23 | 1.39 | 0.28 | 0.79 | 0.29 | 0.35 | 0.36 | 0.43 | 0.37 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nickel (as Ni) | ug/L | Chronic Health | < 150 | 0 | 0 | #DIV/0! |  | #DIV/0!
Cobalt (as Co) | ug/L | Chronic Health | <500 | 0 | 0 | #DIV/0! |  | #DIV/0!
Copper (as Cu) | ug/L | Chronic Health | < 2000 | 0 | 0 | #DIV/0! |  | #DIV/0!
Chromium (as Cr) | ug/L | Chronic Health | < 100 | 0 | 0 | #DIV/0! |  | #DIV/0!
Cadmium (as Cd) | ug/L | Chronic Health | < 5 | 0 | 0 | #DIV/0! |  | #DIV/0!
Lead (as Pb) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! |  | #DIV/0!
Cyanide | ug/L | Acute Health - 1 | < 70 |  |  | #DIV/0! |  | #DIV/0!
Arsenic (as As) | ug/L | Chronic Health | < 10 | 0 | 0 | #DIV/0! |  | #DIV/0!
Mercury (as Hg) | ug/L | Chronic Health | < 6 | 0 | 0 | #DIV/0! |  | #DIV/0!
Selenium (as Se) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! |  | #DIV/0!
Vanadium (as V) | ug/L | Chronic Health | < 200 | 0 | 0 | #DIV/0! |  | #DIV/0!
Antimony (as Sb) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! |  | #DIV/0!
| Acute Health - 1 Chemical |  |  | 60 | 60 | 100% | Excellent |  | ≥ 97% Excellent, ≥ 95% Good, < 95% Unacceptable
| Chronic Health |  |  | 100 | 48 | 48% | Unacceptable
| Aesthetic |  |  | 183 | 162 | 88.52% | Excellent
| Risk Assessment Defined Health (Acute or Chronic) |  |  | 160 | 108 | 67.5% | Unacceptable |  | ≥ 95% Excellent, ≥ 93% Good, < 93% Unacceptable
| Operational Efficiency |  |  | 76 | 74 | 97.37% | Excellent
[6 empty] | 94% | Good

## Matjiesfontein
COMPLIANCE SAMPLE RESULTS FOR WATER (July 2015- June 2016)
Matjiesfontein |  |  | 2014 Blue Drop Limits | Compliance Calculations |  |  |  |  | Jul | Aug | Sept | Oct | Nov | Dec | Jan | Febr | Mar | Apr | May | Jun
Parameter | Unit | Risk | Standard Limits (SANS 241-2011 and SANS 241-2006 Class I) | Total Number of Samples | Number of Samples Complying | % Compliance Achieved | Performance | Average | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap | Matjiesfontein Tap
pH (at 25°C) | pH | Operational | >5.0 - < 9.7 | 5 | 5 | 100% | Excellent | 7.562 | Jul: 7.3; Aug: 7.67; Sept: 6.72; Oct: 8.38; Nov: 7.74
Conductivity | mS/m | Aesthetic | < 170 | 5 | 5 | 100% | Excellent | 111.4 | Jul: 113; Aug: 114; Sept: 107; Oct: 116; Nov: 107
Langelier Saturation Index |  |  | - | 0
Turbidity | NTU | Operational | < 1 | 5 | 5 | 100% | Excellent | 0 | Jul: 0; Aug: 0; Sept: 0; Oct: 0; Nov: 0
|  | Aesthetic | < 5 | 5 | 5 | 100% | Excellent
Colour (as Pt) | mg/L Pt-Co | Aesthetic | < 20 | 0 | 0
CaCO3 Precipitation Potential |  |  | - | 0
Total Alkalinity (as CaCO3) |  |  | - | 0
Total Hardness (as CaCO3) |  |  | - | 0
Calcium Hardness (as CaCO3) |  |  | - | 0
Calcium (as Ca) | mg/L | Aesthetic / Operation | < 150 | 0 | 0 | #DIV/0! | Excellent | #DIV/0!
Magnesium Hardness (as CaCO3) |  |  | - | 0
Magnesium (as Mg) | mg/L | Aesthetic / Health | < 70 | 0 | 0 | #DIV/0! | Excellent | #DIV/0!
Fluoride (as F) | mg/L | Chronic Health | < 1.5 | 5 | 0 | 0% | Excellent | 0.368 | Jul: 0.42; Aug: 0.32; Sept: 0.4; Oct: 0.39; Nov: 0.31
Total Dissolved Solids | mg/L | Aesthetic | < 1 200 | 0 | 0 | #DIV/0! | Excellent | #DIV/0!
Free Chlorine |  | Chronic Health | > 0 - < 0.5 | 0 | 0 | #DIV/0! |  | #DIV/0!
Iron (as Fe) | ug/L | Chronic Health | < 2 000 | 10 | 10 | 100% | Excellent | 0.028 | Jul: 0.05; Aug: 0.02; Sept: 0.04; Oct: 0.03; Nov: 0
|  | Aesthetic | < 300 | 10 | 10 | 100% | Excellent | 0.028 | Jul: 0.05; Aug: 0.02; Sept: 0.04; Oct: 0.03; Nov: 0
Manganese (as Mn) | ug/L | Chronic Health | < 500 | 5 | 5 | 100% | Excellent | 0.000914 | Jul: 0.002; Aug: 0; Sept: 0.00257; Oct: 0; Nov: 0
|  | Aesthetic | < 100 | 5 | 5 | 100% | Excellent
Aluminium (as Al) | ug/L | Operational | < 300 | 4 | 4 | 100% | Excellent | 0.00175 | Jul: 0; Sept: 0.007; Oct: 0; Nov: 0
Escherichia Coli | cfu/100ml | Acute Health - 1 | < 0 | 5 | 5 | 100% | Excellent | 0 | Jul: 0; Aug: 0; Sept: 0; Oct: 0; Nov: 0
Total Coliform Bacteria | cfu/100ml | Operational | < 10 | 5 | 5 | 100% | Excellent | 0 | Jul: 0; Aug: 0; Sept: 0; Oct: 0; Nov: 0
Heterotrophic Plate Count | cfu/ml | Operational | < 1000 | 0 | 0
Total Chlorine | mg/L | Chronic Health | < 5 | 5 | 5 | 100% | Excellent | 0.432 | Jul: 0.07; Aug: 0.56; Sept: 0.7; Oct: 0.05; Nov: 0.78
Dissolved Organic Carbon | mg/L | Chronic Health | < 10 | 5 | 2 | 40% | Unacceptable | 14.86 | Jul: 16.5; Aug: 29.4; Sept: 5.6; Oct: 5.9; Nov: 16.9
Sodium (as Na) | mg/L | Aesthetic | < 200 | 5 | 5 | 100% | Excellent | 141.776 | Jul: 128.16; Aug: 117.18; Sept: 123.73; Oct: 144.68; Nov: 195.13
Potassium (as K) | mg/L | Operational / Health | < 50 | 0 | 0 | #DIV/0! |  | #DIV/0!
Zinc (as Zn) | mg/L | Aesthetic | < 5 | 5 | 5 | 100% | Excellent | 0.0502 | Jul: 0.001; Aug: 0.06; Sept: 0.15; Oct: 0.01; Nov: 0.03
Chloride (as Cl) | mg/L | Aesthetic | < 300 | 5 | 5 | 100% | Excellent | 163.15 | Jul: 143; Aug: 160; Sept: 189.73; Oct: 161.68; Nov: 161.34
Sulphate (as SO42-) | mg/L | Acute Health - 1 | < 500 | 10 | 10 | 100% | Excellent | 33.742 | Jul: 36.33; Aug: 31.85; Sept: 33.13; Oct: 34.36; Nov: 33.04
|  | Aesthetic | < 250 | 10 | 10 | 100% | Excellent | 33.742 | Jul: 36.33; Aug: 31.85; Sept: 33.13; Oct: 34.36; Nov: 33.04
Ammonia Nitrogen (as N) | mg/L | Aesthetic | < 1.5 | 5 | 0 | 0% | Excellent | 0.5338 | Jul: 0.328; Aug: 0.23; Sept: 0.36; Oct: 0.92; Nov: 0.831
Nitrate as N | mg/L | Acute Health - 1 | < 11 | 5 | 5 | 100% | Excellent | 0.622 | Jul: 0.87; Aug: 0.93; Sept: 0.99; Oct: 0.02; Nov: 0.3
Nickel (as Ni) | ug/L | Chronic Health | < 150 | 0 | 0 | #DIV/0! |  | #DIV/0!
Cobalt (as Co) | ug/L | Chronic Health | <500 | 0 | 0 | #DIV/0! |  | #DIV/0!
Copper (as Cu) | ug/L | Chronic Health | < 2000 | 0 | 0 | #DIV/0! |  | #DIV/0!
Chromium (as Cr) | ug/L | Chronic Health | < 100 | 0 | 0 | #DIV/0! |  | #DIV/0!
Cadmium (as Cd) | ug/L | Chronic Health | < 5 | 0 | 0 | #DIV/0! |  | #DIV/0!
Lead (as Pb) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! |  | #DIV/0!
Cyanide | ug/L | Acute Health - 1 | < 70
Arsenic (as As) | ug/L | Chronic Health | < 10 | 0 | 0 | #DIV/0! |  | #DIV/0!
Mercury (as Hg) | ug/L | Chronic Health | < 6 | 0 | 0 | #DIV/0! |  | #DIV/0!
Selenium (as Se) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! |  | #DIV/0!
Vanadium (as V) | ug/L | Chronic Health | < 200 | 0 | 0 | #DIV/0! |  | #DIV/0!
Antimony (as Sb) | ug/L | Chronic Health | < 20 | 0 | 0 | #DIV/0! |  | #DIV/0!
| Acute Health - 1 Chemical |  |  | 20 | 20 | 100% | Excellent |  | Jul: ≥ 97% Excellent, ≥ 95% Good, < 95% Unacceptable
| Chronic Health |  |  | 30 | 22 | 73.33% | Unacceptable
| Aesthetic |  |  | 55 | 50 | 90.91% | Excellent
| Risk Assessment Defined Health (Acute or Chronic) |  |  | 50 | 42 | 84% | Good |  | Jul: ≥ 95% Excellent, ≥ 93% Good, < 93% Unacceptable
| Operational Efficiency |  |  | 19 | 19 | 100% | Excellent
[6 empty] | 97% | Excellent